SECTION 26 36 23

AUTOMATIC TRANSFER SWITCHES

- GENERAL

  - SCOPE

    - Furnish and install one (1) 400A, three pole, open transition, solid neutral automatic transfer switch (ATS). The automatic transfer shall consist of an inherently double throw power transfer switch mechanism and a microprocessor controller to provide automatic operation.  The transfer switch and the controller shall be the products of the same manufacturer.

    - Furnish a stainless steel, NEMA 4X, enclosure for the ATS. The ATS shall provide all of the proper disconnecting, protection, grounding, and bonding.

  - CODES AND STANDARDS

The service entrance automatic transfer switches and controls shall conform to the requirements of:

    - UL 1008 - Standard for Transfer Switch Equipment;

    - IEC 947-6-1 Low-voltage Switchgear and Control gear; Multifunction equipment; Automatic Transfer Switching Equipment;

    - NFPA 70 - National Electrical Code;

    - NFPA 110 - Emergency and Standby Power Systems;

    - IEEE Standard 446 - IEEE Recommended Practice for Emergency and Standby Power Systems for Commercial and Industrial Applications;

    - NEMA Standard ICS10-1993 (formerly ICS2-447) - AC Automatic Transfer Switches;

    - UL 508 Industrial Control Equipment;

    - UL 891 According to this UL standard the equipment shall be labeled ASuitable for use only as service Entrance.@

  - ACCEPTABLE MANUFACTURERS

Automatic Transfer Switches shall be provided by the generator manufacturer.  as part of the generator package.  Generator manufacturers that are listed shall also be listed supplier for the ATS.

In addition, ASCO series 7000 ATS or Russell Electric ATS shall also be acceptable.

  - SUBMITTALS  AND  SHOP DRAWINGS

Provide six (6) copies of automatic transfer switch submittal for Engineer=s review and approval.  ATS can not be released for production unless submittal is approved by Engineer. Submittal shall include:

    - Detailed data sheets for all major components of the transfer switch:

      - Transfer Switch

      - Controller

      - Disconnect and Overcurrent Protection

    - Wiring Diagram

    - List of included and available options

- PRODUCTS

  - Mechanically Held Switches

    - The transfer switch shall be electrically operated and mechanically held.  The electrical operator shall be a momentarily energized, single-solenoid mechanism.  Main operators which include overcurrent disconnect devices, linear motors, or gears shall not be acceptable.  The switch shall be mechanically interlocked to ensure only two possible positions, normal or emergency.

    - All transfer switch sizes shall use only one type of main operator for ease of maintenance and commonality of parts.

    - The switch shall be positively locked and unaffected by momentary outages, so that contact pressure is maintained at a constant value and contact temperature rise is minimized for maximum reliability and operating life.

    - Inspection of all contacts shall be possible from the front of the switch without the disassembly of operating linkages and without the disconnection of power conductors. Switches rated 800 amps and higher shall have front removable and replaceable contacts. All stationary and moveable contacts shall be replaceable without removing power conductors and/or bus bars.

    - Designs utilizing components of molded-case circuit breakers, contactors, or parts thereof, which are not intended for continuous duty, repetitive switching, or transfer between two active power sources, are not acceptable.

    - Where neutral conductors are to be solidly connected as shown on the plans, a neutral conductor plate with fully-rated AL-CU pressure connectors shall be provided.

  - Microprocessor Controller

    - The controller's sensing and logic shall be provided by a single, built-in microprocessor for maximum reliability, minimum maintenance, and the ability to communicate serially through an optional serial communication module;

    - A single controller shall provide twelve selectable nominal voltages for maximum application flexibility and minimal spare part requirements.  Voltage sensing shall be true RMS type and shall be accurate to  1% of nominal voltage.  Frequency sensing shall be accurate to  0.2%.  The panel shall be capable of operating over a temperature range of -20 to +60 degrees C and storage from -55 to +85 degrees C;

    - The controller shall be connected to the transfer switch by an interconnecting wiring harness.  The harness shall include a keyed disconnect plug to enable the controller to be disconnected from the transfer switch for routine maintenance. Sensing and control logic shall be provided on multi-layer printed circuit boards.  Interfacing relays shall be industrial grade plug-in type with dust covers. The panel shall be enclosed with a protective cover and be mounted separately from the transfer switch unit for safety and ease of maintenance. The protective cover shall include a built-in pocket for storage of the operator=s manuals;

    - All customer connections shall be wired to a common terminal block to simplify field-wiring connections;

  - Enclosure

    - The ATS shall be furnished in a single NEMA 4X stainless steel enclosure.

    - All standard and optional door-mounted switches and pilot lights shall be 16-mm industrial grade type or equivalent for easy viewing & replacement. Door controls shall be provided on a separate removable plate which can be supplied loose for open type units.

    - A disconnect link shall be provided to disconnect the normal source neutral connection from the emergency and load neutral connections for 4-mm wire applications. A ground bus shall be provided for connection of the grounding conductor to the grounding electrode. A pressure disconnect link for the neutral to ground bonding jumper shall be provided to connect the normal neutral connection to the ground bus.

  - OPERATIONS

    - Controller Display and Keypad

A four line, 20 character LCD display and keypad shall be an integral part of the controller for viewing all available data and setting desired operational parameters.  Operational parameters shall also be available for viewing and limited control through the serial communications input port.  The following parameters shall only be adjustable via DIP switches on the controller:

      - Nominal line voltage and frequency

      - Single or three phase sensing

      - Operating parameter protection

      - Transfer operating mode configuration (Open transition, Closed transition, or Delayed transition)

All instructions and controller settings shall be easily accessible, readable, and accomplished without the use of codes, calculations, or instruction manuals.

    - Time Delays

      - An adjustable time delay of 0 to 6 seconds shall be provided to override momentary normal source outages and delay all transfer and engine starting signals.  Capability shall be provided to extend this time delay to 60 minutes by providing an external 24 VDC power supply.

      - A time delay shall be provided on transfer to emergency, adjustable from 0 to 60 minutes, for controlled timing of transfer of loads to emergency.

      - Two time-delay modes (which are independently adjustable) shall be provided on re-transfer to normal.  One time delay shall be for actual normal power failures and the other for the test mode function.  The time delays shall be adjustable from 0 to 60 minutes.  Time delay shall be automatically bypassed if the emergency source fails and the normal source is acceptable.

      - A time delay shall be provided on shut down of engine generator for cool down, adjustable from 0 to 60 minutes.

      - A time-delay activated output signal shall also be provided to drive an external relay(s) for selective load disconnect control.  The controller shall have the ability to activate an adjustable 0- to 5-minute time delay in any of the following modes:

        - Prior to transfer only.

        - Prior to and after transfer.

        - Normal to emergency only.

        - Emergency to normal only.

        - Normal to emergency and emergency to normal.

        - All transfer conditions or only when both sources are available.

      - The controller shall also include the following built-in time delays for optional Closed-Transition and Delayed-Transition operation:

        - 1- to 5-minute time delay on failure to synchronize normal and emergency sources prior to closed transition transfer.

        - 0.1- to 9.99-second time delay on an extended parallel condition of both power sources during closed transition operation.

        - 0- to 5-minute time delay for the load disconnect position for delayed transition operation.

      - All time delays shall be adjustable in 1-second increments, except the extended parallel time, which shall be adjustable in .01-second increments

      - All time delays shall be adjustable by using the LCD display and keypad or with a remote device connected to the serial communications port.

    - Additional Features

      - An automatic exerciser that will be programmable to automatically start the generator in time frame selected by the operator. Exerciser shall be capable of setting date and time.

      - A three-position, momentary-type test switch shall be provided for the test / automatic / reset modes.  The test position will simulate a normal source failure.  The reset position shall bypass the time delays on either transfer to emergency or retransfer to normal.

      - A SPDT contact, rated 5 amps at 24 VDC, shall be provided for a low-voltage engine start signal.  The start signal shall prevent dry cranking of the engine by requiring the generator set to reach proper output, and run for the duration of the cool down setting, regardless of whether the normal source restores before the load is transferred.

      - Auxiliary contacts, rated 10 amps, 250 VAC shall be provided consisting of one contact closed when the ATS is connected to the normal source and one contact closed when the ATS is connected to the emergency source.

      - LED indicating lights (16 mm industrial grade, Type 12) shall be provided, one to indicate when the ATS is connected to the normal source (green) and one to indicate when the ATS is connected to the emergency source (red).

      - LED indicating lights (16 mm industrial grade, type 12) shall be provided and energized by controller outputs. The lights shall provide true source availability of the normal and emergency sources, as determined by the voltage sensing trip and reset settings for each source.

      - The following features shall be built-in to the controller but capable of being activated through keypad programming or the serial port only when required by the user:

        - Provide the ability to select commit/no commit to transfer to determine whether the load should be transferred to the emergency generator if the normal source restores before the generator is ready to accept the load.

        - Terminals shall be provided for a remote contact which opens to signal the ATS to transfer to emergency and for remote contacts which open to inhibit transfer to emergency and/or retransfer to normal.  Both of these inhibit signals can be activated through the keypad or serial port.

        - The controller shall be capable of accepting a normally open contact that will allow the transfer switch to function in a non-automatic mode using an external control device.

        - System Status - The controller LCD display shall include a System Status screen :

          - Normal Failed;

          - Load on Normal;

          - TD Normal to Emergency;

          - Time to transfer;

    - Additional Requirements

      - Withstand and Closing Ratings

        - The ATS shall be rated to close on and withstand minimum of 65,000 kA RMS symmetrical short circuit current at the ATS terminals with the type of overcurrent protection shown on the plans;

        - The ATS shall be UL listed in accordance with UL 1008 and be labeled in accordance with that standard's 12 and 3 cycle, long-time ratings.  ATSs which are not tested and labeled with 12 and 3 cycle (any breaker) ratings and have series, or specific breaker ratings only, are not acceptable.

      - Test and Certifications

        - The complete ATS shall be factory tested to ensure proper operation of the individual components and correct overall sequence of operation and to ensure that the operating transfer time, voltage, frequency and time delay settings are in compliance with the specification requirements.

        - Upon request, the manufacturer shall provide a notarized letter certifying compliance with all of the requirements of this specification including compliance with the above codes and standards, and withstand and closing ratings.  The certification shall identify, by serial number(s), the equipment involved.  No exceptions to the specifications, other than those stipulated at the time of the submittal, shall be included in the certification.

        - The ATS manufacturer shall be certified to ISO 9001 International Quality Standard and the manufacturer shall have third party certification verifying quality assurance in design/development, production, installation, and servicing in accordance with ISO 9001.

        - The transfer switch system must contain a disconnect device on the normal source as well as a disconnect link on the utility neutral and a disconnect link between neutral and ground.  The ATS manufacturer shall be certified to comply with NEC 230.70, 230.70(B), 230.75 and 230.95.

      - Service Representation

        - The ATS manufacturer shall maintain a national service organization of company-employed personnel located throughout the contiguous United States.  The service center's personnel must be factory trained and must be on call 24 hours a day, 365 days a year.

        - The manufacturer shall maintain records of each switch, by serial number, for a minimum of 20 years.

- EXECUTION

  - INSTALLATION

    - Install as indicated and in accordance with manufacturer's instructions and recommendations.

    - Switch enclosures will not vibrate, turn, or shake when the handle is actuated.

    - Label each safety switch with engraved micarta nameplate to identify function and/or load served.

    - Place voltage warning label on switch.

END OF SECTION